1. Role of the InteliNeo 6000 in the Technoserve Microgrid Architecture

In the proposed Technoserve system, the InteliNeo 6000 is not a power-conversion device and does not replace inverters, protection relays, or switchgear. Its role is more fundamental:

it is the supervisory and coordinating controller that determines how and when each energy asset is allowed to operate together as one electrical system.

According to ComAp’s own definition, the InteliNeo 6000 is a microgrid controller for parallel hybrid microgrid applications, designed to coordinate:

- Battery Energy Storage Systems (BESS),

- Renewable generation such as PV,

- Utility mains connections, and

- Conventional generators (when used in MINT architectures).

In your case, with existing generators, existing PV, and a new BESS, the controller would be deployed in a MINT (Multiple Island-Parallel) configuration. This is the architecture explicitly intended for systems where multiple source types operate together and must remain stable if any single source connects or disconnects

intelineo 6000 2.2.0 global guide

.

The controller continuously measures:

- Bus voltage, frequency, phase sequence, and harmonic distortion,

- Active and reactive power flows,

- State of charge (SOC) and operating limits of the BESS,

- Status and availability of breakers and sources.

Based on these measurements, it executes pre-defined control strategies that govern power sharing, import/export limits, islanding behaviour, and recovery after disturbances.

2. Integration with Existing Electrical Infrastructure

2.1 Electrical Interface Philosophy

The InteliNeo 6000 integrates into existing infrastructure through measurement, control, and communication layers, not by altering the fundamental protection philosophy of the plant.

Electrically, it connects to:

- Voltage transformers (VTs) on the BESS side and the mains/bus side,

- Current transformers (CTs) for BESS output and auxiliary (bus/mains) measurements,

- Breaker status feedbacks (MCB, BCB, PVCB as applicable),

- Breaker control outputs, where allowed by the design.

Importantly, the controller does not bypass or override hardwired protections. All fast fault clearing (short-circuit, earth fault, inverter self-protection) remains the responsibility of:

- Inverter internal protections,

- Generator controllers,

- Protection relays and switchgear.

The InteliNeo 6000 operates above this layer, ensuring that sources are only commanded to operate within allowed electrical conditions.

2.2 Integration of the BESS (CATL + EPC CAB 1000)

The controller natively supports one BESS per InteliNeo 6000, with explicit internal logic governing:

- BESS starting sequence,

- DC precharge (stabilisation),

- Grid-following and grid-forming operation,

- Active and reactive power control,

- SOC-based charging and discharging limits.

A key function for client confidence is the explicit BESS state machine, which controls how the battery transitions between states such as:

- Standby,

- Charging,

- Discharging,

- Grid-forming (island operation),

- Fault or inhibited states.

This is not a “best-effort” behaviour; it is a defined sequence described in the application functions section of the manual, ensuring that the BESS is never connected to the bus in an electrically unsafe state

intelineo 6000 2.2.0 global guide

.

The controller supports both:

- P–Q control, where active and reactive power are directly commanded, and

- U–f control, where the BESS forms voltage and frequency in island mode.

Which method is used depends on:

- Whether the system is grid-connected or islanded,

- Whether the BESS inverter supports grid-forming operation.

2.3 Existing PV Integration

Existing PV inverters are integrated via:

- Modbus RTU or Modbus TCP communication, or

- Discrete breaker control and power measurement.

The InteliNeo 6000 supports:

- PV output limitation (curtailment),

- Priority use of PV generation ahead of gensets or mains import,

- PV disconnection during islanding if grid-code or inverter limitations require it.

Importantly, the controller does not assume PV is always controllable. If PV inverters only support on/off control or limited power setpoints, the system logic is configured accordingly. This avoids the false impression that the controller can “force” behaviour that the inverter cannot support

intelineo 6000 2.2.0 global guide

.

2.4 Existing Generators

In a MINT configuration, generators retain their own dedicated genset controllers. The InteliNeo 6000 coordinates with them via:

- CAN inter-controller communication, or

- Modbus communication.

This distributed architecture ensures that:

- Loss or trip of a generator does not collapse the microgrid control system,

- Each source remains locally protected,

- Power sharing and load control are coordinated rather than centralized in a single point of failure.

3. Power Management and Operating Modes

3.1 Operating Modes (On-Grid and Off-Grid)

The InteliNeo 6000 explicitly distinguishes between:

- On-grid operation (parallel with utility mains), and

- Off-grid (islanded) operation.

Transitions between these states are managed through:

- Loss-of-mains detection,

- Controlled disconnection and reconnection logic,

- Synchronisation checks before reconnection.

The controller supports black-start scenarios, provided the BESS inverter itself is capable of grid-forming operation. In such cases, the InteliNeo 6000 ensures:

- Controlled energisation of the bus,

- Gradual load pickup using ramped power increases,

- Coordination of PV and genset reconnection after stabilisation

intelineo 6000 2.2.0 global gui…

.

3.2 Energy Optimisation Functions

The following functions are explicitly supported and configurable:

- Balance mode
Prioritises renewable generation and BESS use before importing from mains or starting gensets.

- Peak shaving
Limits import from the utility grid by supplementing demand with BESS power.

- Load shedding
Ensures critical loads remain supplied when available generation is insufficient.

- Import / Export control
Maintains grid exchange within contractual or technical limits.

These are not “AI-driven” or adaptive in an uncontrolled way. They are rule-based strategies with clearly defined setpoints and limits configured during commissioning.

4. Reliability, Redundancy, and Cybersecurity

4.1 Redundancy and Fault Tolerance

The InteliNeo 6000 supports:

- Hot-swap controller redundancy, where a secondary unit can take over if the primary fails,

- Redundant CAN communication lines, reducing single-point failures in inter-controller communication.

In addition, the controller maintains:

- Event-based history logs,

- CAN bus diagnostic logs,

- Alarm histories with time stamping.

This significantly reduces troubleshooting time and improves operational transparency

intelineo 6000 2.2.0 global gui…

.

4.2 Cybersecurity and Access Control

The controller is designed in alignment with ISA 62443 security principles, including:

- User-based access levels,

- Encrypted controller data,

- Protected PLC logic and setpoints,

- Separation of trusted and untrusted network interfaces.

Remote access via AirGate 2.0 allows monitoring and control without exposing the site to direct public IP addressing, reducing attack surface while enabling remote support and fleet management

intelineo 6000 2.2.0 global gui…

.

5. Why the InteliNeo 6000 Is Central to the Solution

From a system perspective, the InteliNeo 6000 is best understood as the “system conductor”:

- Inverters convert power,

- Batteries store energy,

- Generators produce energy,

- Switchgear protects equipment,

but only the microgrid controller decides how all of these elements are allowed to interact safely and efficiently.

Without a controller of this class:

- Islanding becomes risky or manual,

- Power sharing becomes unstable,

- Renewable utilisation drops,

- Recovery after faults becomes slower and more error-prone.

The InteliNeo 6000 does not remove engineering responsibility or eliminate the need for correct protection design—but it enables a complex hybrid system to behave as one coherent electrical plant rather than a collection of independent assets.

Final reassurance to the end user

The controller does not promise uninterrupted power under all circumstances, nor does it override physical protections. What it does provide—when correctly engineered and commissioned—is:

- Predictable behaviour,

- Coordinated response to disturbances,

- Transparent control logic,

- Compliance with recognised electrical and grid standards.

For a hybrid BESS-PV-genset installation such as Technoserve’s, it is not an optional accessory; it is the enabling layer that makes the solution technically viable and operationally understandable.